## BOQ
ANNEXURE-2
NAME OF THE PROJECT: HVAC WORK AT NIRMAL BUILDING FOR ECGC Limited (hereinafter referred to as ‘ECGC / the Corporation’), |  |  |  |  | 18.08.20
Subject: BILL OF QUANTITY - HVAC WORKS
Sr. No. | Description | Unit | Qty | Unit Rate | Total
A
1 | INVERTER BASED DUCTABLE AIRCONDITIONERS
1.1 | Supply of Self Contained Inverter Ductable type Split Units of capacities mentioned below having Construction of base panel of fabricated steel structures. Casing panel will be of Heavy gauge SS welded construction & Indoor unit having integral drain pump.Casings will be complete with plenum, discharge outlets, grills space for fans, refrigeration equipments & cooling coils. Outdoor Condensing unit alongwith cordless remote with Power panel & internal control wiring. First Charge of refrigerant gas, M.S. stand for ODU, Refrigerant gas R410A & all mounting arrangements etc. Make - Daikin,Carrier, Bluestar
1.1.1 | 11 Tr | Nos. | 3 |  | 0
1.1.2 | 8.5 Tr | Nos. | 3 |  | 0
1.2 | Installation, Testing & Commissioning of Self contained inverter Ductable type SPLIT Airconditioners with outdoor condensing units along with Cordless remote control, Ductable type indoor units, CFC free refrigerant, controls, copper earthing, single phase preventor, remote control, safeties, M.S. stand for ODU.,
1.2.1 | 11 Tr | Nos. | 3 |  | 0
1.2.2. | 8.5 Tr | Nos. | 3 |  | 0
1.3 | Supply, Installation, Testing & Commissioning of mirror finish inside / outside refrigerant piping including liquid & suction pipes with insulation out of copper pipes with 19 mm thick class "O" armaflex nitrile rubber. Pipe linewill be tested for requisite pressure & will be supported at every 6 ft in intervals. (Quantity shall be measured one way & considering single circuit)
1.3.1 | 11 Tr | Rmt | 10 |  | 0
1.3.2 | 8.5 Tr | Rmt | 10 |  | 0
1.4 | Supply, Installation, Testing & Commissioning of Electrical copper cables between Panel to outdoor, indoor units & Control Cable from Indoor to Outdoor Units with earthing termination as per below mentioned Specifications (Quantity shall be measured one way & considering single circuit)
1.4.1 | 4 Core X 10 Sq. mm armoured | Rmt | 10 |  | 0
1.4.2 | 4 Core X 1.5 Sq mm flexible | Rmt | 10 |  | 0
1.4.3 | 4 Core X 2.5 Sq mm flexible | Rmt | 10 |  | 0
1.4.4 | 7 Core X 1.5 Sq mm flexible | Rmt | 10 |  | 0
1.4.5 | 8 Gauge Copper cable for Earthing | Rmt | 10 |  | 0
1.5 | Supply & Installation of Insulated Hard PVC drain Piping with supporting clamps.
1.5.1 | 50 mm | Rmt | 10 |  | 0
1.6 | Supply Of additional Refrigerant in case Piping length increases above standard limitation
1.6.1 | R-410 A | Lot | 2 |  | 0
| TOTAL FOR 1.0 |  |  |  | 0
2
2.1 | SHEET METAL DUCTING with SMACNA STANDARDS including Acoustic insulation
Supply, fabrication, Installation, and testing of sheet metal rectangular ducts with 20 mm armasounding Accoustic Insulation accordance with the approved shop drawings and as per the specifications
`
2.1.1 | 1 - 750 (upto 30") -- 26 G C&SS | Sq.mt |  |  | 0
2.1.2 | 751 - 1000 (31" - 40") -- 26 G | Sq.mt |  |  | 0
2.1.3 | 1001 - 1500 (41" - 60") -- 24 G | Sq.mt | 30 |  | 0
2.1.4 | 1501 - 1800 (61" - 72") -- 22 G | Sq.mt | 20 |  | 0
2.1.5 | 1801 - 2100 (73" - 84") -- 20 G | Sq.mt | 20 |  | 0
2.1.6 | 2101 - 2400 (85" - 96") -- 18 G | Sq.mt |  |  | 0
2.1.7 | 2401 & Above (97" & above) --18 G | Sq.mt |  |  | 0
2.2 | Supply & Installation of Canvas Connections | Nos | 6 |  | 0
0
2.3 | Dis-mantling, Cleaning and Installation of supply air gril and returm air grill | Lot. | 2 |  | 0
0
2.4 | Supply, and Installation of Collar damper | Lot. | 2 |  | 0
0
2.5 | Supply and Installation of Volume control damper | Lot. | 2 |  | 0
0
2.6 | Supply, installation, testing & commissioning of prefabricated (Galvanised ) .G.I. Ladder/Perforated trays with 50/75 mm C channels & Ruges at 200 mm cc and including prefabricated accessories like bends,Tee,Right angle & tray coupling arrangements etc.(Bends fabricated at site will not be allowed). |  |  |  | 0
2.6.1 | 50mm, 50x50 perforated tray. | Rmt | 30 |  | 0
0
2.7 | Supply, installation, testing & commissioning of Cable Tray Covers suitable for following size trays |  |  |  | 0
2.7.1 | 50mm perforated tray. | Rmt. | 30 |  | 0
0
2.8 | Supply & installation of End termination for cables as above with Brass, heavy duty, Single / double compression glands & for outdoor Double compression, Al/ Cu lugs, other consumable like insulation adhesive tape, crimping, gland hole drilling, ferrulling, marking, etc. | Lot. | 2 |  | 0
| TOTAL FOR 2.0 |  |  |  | 0
| GRAND TOTAL (1.0+2.0) |  |  |  | 0